Class I, Divisions 1 & 2, Group D

Class I, Zones 1 & 2, Group IIA

| KW | Ignition Temperature Code oF (oC) | Volts | Phase | Amps (1) | Catalog Number | Availability Code (2) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 3 | T3 392 (200) | 208 | 1 | 15 | HX-236-F01T-0037C | C |  |
|  |  | 240 | 1 | 13 | HX-236-F01T-0037J |  |  |
|  |  | 480 | 1 | 6 | HX-236-F01T-0037T |  |  |
|  |  | 208 | 3 | 8 | HX-236-F01T-0037D |  |  |
|  |  | 240 | 3 | 7 | HX-236-F01T-0037K |  |  |
|  |  | 480 | 3 | 4 | HX-236-F01T-0037U |  |  |
|  |  | 600 | 3 | 3 | HX-236-F01T-0037Z |  |  |
| 5 | T2C 446 (230) | 208 | 1 | 24 | HX-236-F01T-0055C |  |  |
|  |  | 240 | 1 | 21 | HX-236-F01T-0055J |  |  |
|  |  | 480 | 1 | 11 | HX-236-F01T-0055T |  |  |
|  |  | 208 | 3 | 14 | HX-236-F01T-0055D |  |  |
|  |  | 240 | 3 | 12 | HX-236-F01T-0055K |  |  |
|  |  | 480 | 3 | 8 | HX-236-F01T-0055U |  |  |
|  |  | 600 | 3 | 5 | HX-236-F01T-0055Z |  |  |
| 7 | T2 572 (300) | 208 | 1 | 34 | HX-236-F01T-0072C |  |  |
|  |  | 240 | 1 | 29 | HX-236-F01T-0072J |  |  |
|  |  | 480 | 1 | 15 | HX-236-F01T-0072T |  |  |
|  |  | 208 | 3 | 20 | HX-236-F01T-0072D |  |  |
|  |  | 240 | 3 | 17 | HX-236-F01T-0072K |  |  |
|  |  | 480 | 3 | 9 | HX-236-F01T-0072U |  |  |
|  |  | 600 | 3 | 7 | HX-236-F01T-0072Z |  |  |
| 10 | T1 842 (450) | 240 | 1 | 42 | HX-236-F01T-0101J |  |  |
|  |  | 480 | 1 | 21 | HX-236-F01T-0101T |  |  |
|  |  | 208 | 3 | 28 | HX-236-F01T-0101D |  |  |
|  |  | 240 | 3 | 24 | HX-236-F01T-0101K |  |  |
|  |  | 480 | 3 | 12 | HX-236-F01T-0101U |  |  |
|  |  | 600 | 3 | 10 | HX-236-F01T-0101Z |  |  |
| 12 | T1 842 (450) | 480 | 1 | 25 | HX-236-F01T-0121T |  |  |
|  |  | 240 | 3 | 29 | HX-236-F01T-0121K |  |  |
|  |  | 480 | 3 | 15 | HX-236-F01T-0121U |  |  |
|  |  | 600 | 3 | 12 | HX-236-F01T-0121Z |  |  |

(1) The Amps shown are for the heating elements only. The 120V 1PH 60HZ motor draws 3.8 Amps and requires a separate 120V power supply.

(2) Availability Code: C = Custom

(3) Price includes swivel mounting bracket.

Factory Built-in Options

| Code | Option | Description | Availability Code |  |
| --- | --- | --- | --- | --- |
| C | Dirty Duty Corrosion- Resistant Construction | Includes epoxy-coated fan blade, wiring conduit and fittings, NEMA 4X, 7, 9 enclosure. | C |  |
| CM | Marine Duty Construction | Dirty Duty Construction with manual reset thermal cutout. Meets U.S. Coast Guard requirements per 46 CFR-111.87 and is ABS Approved. | C |  |
| M | Manual Reset Cutout | Can be specified to replace secondary automatic cutout. | C |  |
| T | Adjustable Thermostat | Factory installed and prewired to the control enclosure. Thermostat is adjustable from 50o to 90oF (10o to 32oC) range) | C |  |

Accessory Remote Room Thermostat

| Catalog Number | Description | Availability Code |  |
| --- | --- | --- | --- |
| 1007002 | Explosion-proof wall-mounted thermostat - Classes I & II, Divisions 1 & 2, Groups C,D,E,F & G 50o- 90oF (10o - 32oC) range | AS |  |

Dimensions, Airflow and Weights

| KW |  | 3 | 5 | 7 | 10 | 12 |
| --- | --- | --- | --- | --- | --- | --- |
| Ignition Temperature Code |  | T3 | T2C | T2 | T1 | T1 |
| Approximate Air Temperature Rise °F (°C) |  | 9 (5) | 15 (8) | 22 (12) | 31 (17) | 37 (21) |
| Airflow Characteristics | Air Volume CFM (cubic meters/hr) | 1050 (1784) | 1050 (1784) | 1050 (1784) | 1050 (1784) | 1050 (1784) |
|  | Air Throw Feet (m) | 25 (8) | 25 (8) | 25 (8) | 25 (8) | 25 (8) |
|  | Outlet Velocity FPM (meters/min) | 1140 (348) | 1140 (348) | 1140 (348) | 1140 (348) | 1140 (348) |
| Motor/Fan | RPM | 1725 | 1725 | 1725 | 1725 | 1725 |
|  | HP | 1/6 | 1/6 | 1/6 | 1/6 | 1/6 |
|  | Fan Blade Dia. Inch (cm) | 12 (31) |  |  |  |  |
| Weight | Net Lbs. (kgs) | 96 (44) |  |  |  |  |
|  | Shipping Lbs (kgs) | 110 (50) |  |  |  |  |

8” Min

(20.3 cm)

120V Motor: Control Wiring When Optional Built-On Thermostat is Used

1-5/16”

(3.3 cm)

Min

Swivel Bracket

(Ceiling Mounted)

5-3/4”

(14.6 cm)

18” Ref.

(45.7 cm)

20”

(50.8 cm)

9-1/4”

(48.9 cm)

13”

(33 cm)

120V Motor: Control Wiring When Optional Built-On Thermostat is Used

Optional Built-On Thermostat

AIRFLOW

8” Min

(20.3 cm)

Heater

Wiring

22”

55.9 (cm)

28-1/4”

(71.8 cm)

Max

4-3/8”

(11.1 cm)

Min