Built-in thermostat is not included.

| Watts | Volts | Total Amps (1) | CFM | Approximate Air Temperature Rise oF (oC) | Weight lbs (kg) | Catalog Number |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 500 | 120 | 4.6 | 40 | 40 (22) | 9 (4) | HX-934U00500B¶ |  |
| 500/375 | 240/208 | 2.3/2.0 | 40 | 40/30 (22/17) | 9 (4) | HX-934U00500V¶ |  |
| 750 | 120 | 6.7 | 40 | 60 (33) | 9 (4) | HX-934U00750B¶ |  |
| 750/563 | 240/208 | 3.3/2.9 | 40 | 60/45 (33/25) | 9 (4) | HX-934U00750V¶ |  |
| 1000 | 120 | 8.7 | 40 | 80 (44) | 9 (4) | HX-934U01000B¶ |  |
| 1000/750 | 240/208 | 4.5/3.8 | 40 | 80/60 (44/33) | 9 (4) | HX-934U01000V¶ |  |
| 1250 | 120 | 10.8 | 80 | 50 (28) | 9 (4) | HX-934U01250B¶ |  |
| 1250/938 | 240/208 | 5.4/4.7 | 80 | 50/37 (28/21) | 9 (4) | HX-934U01250V¶ |  |
| 1500 | 120 | 12.9 | 80 | 60 (33) | 9 (4) | HX-934U01500B¶ |  |
| 1500/1125 | 240/208 | 6.5/5.6 | 80 | 60/45 (33/25) | 9 (4) | HX-934U01500V¶ |  |
| 2000/1500 | 240/208 | 8.5/7.4 | 80 | 80/60 (44/33) | 9 (4) | HX-934U02000V¶ |  |

(1) Total Amps = Heating element amps and motor amps.

All models listed are single-phase.

¶ Standard colors - Add W to end of catalog number for white finish, A for almond finish to the end of catalog number.

Factory Built-in Options

| Code | Description |  |
| --- | --- | --- |
| D3 | Disconnect Switch, 277V, Double-pole, 20 Amp |  |
| T1 | Tamperproof Thermostat, Single-pole, 25 Amp with off position |  |
| T2 | Tamperproof Thermostat, Double-pole, 25 Amp with off position |  |
| T5 | Adjustable Thermostat, Single-pole, 25 Amp with off position |  |
| T6 | Adjustable Thermostat, Double-pole, 25 Amp with off position |  |

Double-pole thermostats include positive off feature.

Field-Installed Options

(shipped loose for field Installation into heater)

| Catalog Number | Description |  |
| --- | --- | --- |
| 934-124647¶ | Surface Mounting Box |  |
| 934-124648¶ | Adjustable Thermostat Kit, Single-pole, 25 Amp with off position |  |
| 934-124649¶ | Tamperproof Thermostat Kit, Single-pole, 25 Amp with off position |  |
| 934-124650¶ | Adjustable Thermostat Kit, Double-pole, 25 Amp with off position |  |
| 934-124651¶ | Tamperproof Thermostat Kit, Double-pole, 25 Amp with off position |  |

¶ Standard colors - Add W to end of catalog number for white finish, A for almond finish to the end of catalog number.

Architect’s and Engineer’s Specifications

The specified heating equipment shall include an electric, fan-forced air wall heater suitable for space heating as manufactured by HEATREX.  The wall heater shall be designed for wall recess or surface mounting.  Heaters shall be third party approved to UL standard 2021.  CSA-US or equivalent is acceptable.

Heater Housing shall be constructed from heavy 20 gauge steel.

Grille shall have a white or almond epoxy/powder paint finish.  Grille openings shall be less than 0.25” to discourage tampering with the elements (pencil-proof).  Contact factory for custom colors.

Heater Element shall be of finned tubular type.

Fan and Motor shall be thermally protected and have permanently lubricated ball bearings.  Fan shall operate at 40 CFM for heaters up to 1000W and 80 CFM for all other models.

Thermal Cutout shall be of the bi-metal type and built into the system.

Mounting Positions

Four mounting positions available.

Pictures showing front panel.

Directional vane air flow.

Optional Surface Mounting	Recess Mounting