HX-912U (Flat Top)

How to order: Model + Heater Code with color code + Options (example: HX-912U03000CW-1198-T1)

| Length In. (mm) | Density |  | Watts | Heater Code |  |  |  |  |  |  |  |  | Watts at 240/208V | Heater Code |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | W/Ft | W/m |  |  | 208V (1 ph) | Amps |  | 240V (1 ph) | Amps |  | 277V (1 ph) | Amps |  |  | 240/208V (1 ph) | Amps |
| 27.2 (690) | 500 | 1000 | 1640 |  | 01000C‡-690 | 4.8 |  | 01000J‡-690 | 4.2 |  | 01000N‡-690 | 3.6 | 1000/750 |  | 01000V‡-690 | 4.2/3.6 |
|  | 750 | 1500 | 2450 |  | 01500C‡-690 | 7.2 |  | 01500J‡-690 | 6.3 |  | 01500N‡-690 | 5.4 | 1500/1125 |  | 01500V‡-690 | 6.3/5.4 |
|  | 1000 | 2000 | 3280 |  | 02000C‡ | 9.6 |  | 02000J‡ | 8.3 |  | 02000N‡ | 7.2 | 2000/1500 |  | 02000V‡ | 8.3/7.2 |
| 37.2 (944) | 500 | 1500 | 1640 |  | 01500C‡-944 | 7.2 |  | 01500J‡-944 | 6.3 |  | 01500N‡-944 | 5.4 | 1500/1125 |  | 01500V‡-944 | 6.3/5.4 |
|  | 750 | 2250 | 2450 |  | 02250C‡-944 | 10.8 |  | 02250J‡-944 | 9.4 |  | 02250N‡-944 | 8.1 | 2250/1690 |  | 02250V‡-944 | 9.4/8.1 |
|  | 1000 | 3000 | 3280 |  | 03000C‡ | 14.4 |  | 03000J‡ | 12.5 |  | 03000N‡ | 10.8 | 3000/2250 |  | 03000V‡ | 12.5/10.8 |
| 47.2 (1198) | 500 | 2000 | 1640 |  | 02000C‡-1198 | 9.6 |  | 02000J‡-1198 | 8.3 |  | 02000N‡-1198 | 7.2 | 2000/1500 |  | 02000V‡-1198 | 8.3/7.2 |
|  | 750 | 3000 | 2450 |  | 03000C‡-1198 | 14.4 |  | 03000J‡-1198 | 12.5 |  | 03000N‡-1198 | 10.8 | 3000/2250 |  | 03000V‡-1198 | 12.5/10.8 |
|  | 1000 | 4000 | 3280 |  | 04000C‡ | 19.2 |  | 04000J‡ | 16.7 |  | 04000N‡ | 14.4 | 4000/3000 |  | 04000V‡ | 16.7/14.4 |
| 57.2 (1452) | 500 | 2500 | 1640 |  | 02500C‡-1452 | 12.0 |  | 02500J‡-1452 | 10.4 |  | 02500N‡-1452 | 9.0 | 2500/1875 |  | 02500V‡-1452 | 10.4/9.0 |
|  | 750 | 3750 | 2450 |  | 03750C‡-1452 | 18.0 |  | 03750J‡-1452 | 15.6 |  | 03750N‡-1452 | 13.5 | 3750/2817 |  | 03750V‡-1452 | 15.6/13.5 |
|  | 1000 | 5000 | 3280 |  | 05000C‡ | 24.0 |  | 05000J‡ | 20.8 |  | 05000N‡ | 18.1 | 5000/3750 |  | 05000V‡ | 20.8/18.0 |
| 65.2 (1655) | 500 | 3000 | 1640 |  | 03000C‡-1655 | 14.4 |  | 03000J‡-1655 | 12.5 |  | 03000N‡-1655 | 10.8 | 3000/2250 |  | 03000V‡-1655 | 12.5/10.8 |
|  | 750 | 4500 | 2450 |  | 04500C‡-1655 | 21.6 |  | 04500J‡-1655 | 18.8 |  | 04500N‡-1655 | 16.2 | 4500/3380 |  | 04500V‡-1655 | 18.8/16.3 |
|  | 1000 | 6000 | 3280 |  | 06000C‡ | 28.8 |  | 06000J‡ | 25.0 |  | 06000N‡ | 21.7 | 6000/4500 |  | 06000V‡ | 25.0/21.6 |

| Length In. (mm) | Density |  | Watts | Heater Code |  |  |  |  |  |  |  |  | Watts at 240/208V | Heater Code |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | W/Ft | W/m |  |  | 208V (3 ph) | Amps |  | 240V (3 ph) | Amps |  | 480V (3 ph) | Amps |  |  | 240/208V (3 ph) | Amps |
| 27.2 (690) | 500 | 1640 | 1000 |  | 01000D‡-690 | 2.8 |  | 01000K‡-690 | 2.4 |  | 01000U‡-690 | 1.2 | 1000/750 |  | 01000P‡-690 | 2.8/2.1 |
|  | 750 | 2450 | 1500 |  | 01500D‡-690 | 4.2 |  | 01500K‡-690 | 3.6 |  | 01500U‡-690 | 1.8 | 1500/1125 |  | 01500P‡-690 | 3.6/3.1 |
|  | 1000 | 3280 | 2000 |  | 02000D‡ | 5.6 |  | 02000K‡ | 4.8 |  | 02000U‡ | 2.4 | 2000/1500 |  | 02000P‡ | 4.8/4.2 |
| 37.2 (944) | 500 | 1640 | 1500 |  | 01500D‡-944 | 4.2 |  | 01500K‡-944 | 3.6 |  | 01500U‡-944 | 1.8 | 1500/1125 |  | 01500P‡-944 | 3.6/3.1 |
|  | 750 | 2450 | 2250 |  | 02250D‡-944 | 6.2 |  | 02250K‡-944 | 5.4 |  | 02250U‡-944 | 2.7 | 2250/1690 |  | 02250P‡-944 | 5.4/4.7 |
|  | 1000 | 3280 | 3000 |  | 03000D‡ | 8.3 |  | 03000K‡ | 7.2 |  | 03000U‡ | 3.6 | 3000/2250 |  | 03000P‡ | 7.2/6.2 |
| 47.2 (1198) | 500 | 1640 | 2000 |  | 02000D‡-1198 | 5.6 |  | 02000K‡-1198 | 4.8 |  | 02000U‡-1198 | 2.4 | 2000/1500 |  | 02000P‡-1198 | 4.8/4.2 |
|  | 750 | 2450 | 3000 |  | 03000D‡-1198 | 8.3 |  | 03000K‡-1198 | 7.2 |  | 03000U‡-1198 | 3.6 | 3000/2250 |  | 03000P‡-1198 | 7.2/6.2 |
|  | 1000 | 3280 | 4000 |  | 04000D‡ | 11.1 |  | 04000K‡ | 9.6 |  | 04000U‡ | 4.8 | 4000/3000 |  | 04000P‡ | 9.6/8.3 |
| 57.2 (1452) | 500 | 1640 | 2500 |  | 02500D‡-1452 | 6.9 |  | 02500K‡-1452 | 6.0 |  | 02500U‡-1452 | 3.0 | 2500/1875 |  | 02500P‡-1452 | 6.0/5.2 |
|  | 750 | 2450 | 3750 |  | 03750D‡-1452 | 10.4 |  | 03750K‡-1452 | 9.0 |  | 03750U‡-1452 | 4.5 | 3750/2817 |  | 03750P‡-1452 | 9.0/7.8 |
|  | 1000 | 3280 | 5000 |  | 05000D‡ | 13.9 |  | 05000K‡ | 12.0 |  | 05000U‡ | 6 | 5000/3750 |  | 05000P‡ | 12.0/10.4 |
| 65.2 (1655) | 500 | 1640 | 3000 |  | 03000D‡-1655 | 8.3 |  | 03000K‡-1655 | 7.2 |  | 03000U‡-1655 | 3.6 | 3000/2250 |  | 03000P‡-1655 | 7.2/6.2 |
|  | 750 | 2450 | 4500 |  | 04500D‡-1655 | 12.5 |  | 04500K‡-1655 | 10.8 |  | 04500U‡-1655 | 5.4 | 4500/3380 |  | 04500P‡-1655 | 10.8/9.4 |
|  | 1000 | 3280 | 6000 |  | 06000D‡ | 16.7 |  | 06000K‡ | 14.4 |  | 06000U‡ | 7.2 | 6000/4500 |  | 06000P‡ | 14.4/12.5 |

Other  voltages available, consult factory.

‡Standard colors - Add W for white finish or A for almond finish to the catalog number when ‡ is indicated.

Factory Built-in Options

| Code | Description |  |
| --- | --- | --- |
| D1 | Disconnect Switch, Three-pole, 600V, 40 Amp |  |
| F | Front Air Outlet (CAI Only) |  |
| R1 | 24V Relay, 240V, 22 Amp; 277V, 19 Amp |  |
| R2 | 24V Relay with Transformer, 240V, 22 Amp; 277V, 19 Amp |  |
| R3 | 24V Double-pole Relay, 240V, 25 Amp; 480V, 12.5 Amp |  |
| R4 | 240V Relay, Single-pole, 240V, 25 Amp; 480V, 12.5 Amp |  |
| R5 | 240V Double-pole Relay, 240V, 25 Amp; 480V, 12.5 Amp |  |
| R6 | Pneumatic Relay, 480V, 25 Amp |  |
| S | Smooth Finish on Heater Back |  |
| T1 | Tamperproof Thermostat, Single-pole, 240V, 30 Amp |  |
| T2 | Tamperproof Thermostat, Double-pole, 480V, 15 Amp (2) |  |
| X1 | 240V Transformer – 50 VA |  |
| X2 | 24V Transformer – 50 VA |  |

(2) Use with three-phase heaters.

Field-Installed Options

(shipped loose for field installation into heater)

| Catalog Number | Description |  |  |
| --- | --- | --- | --- |
| 911-124546¶ | CASI inside corner |  |  |
| 911-218358¶ | CASI outside corner |  |  |
| 912-124546¶ | CAI Corner inside |  |  |
| 912-124547¶ | Round Pedestal Kit | 3-4” High |  |
| 912-124548¶ | Sub Base Heater Length In. (mm) | 27.2 (690) |  |
| 912-124549¶ |  | 37.2 (944) |  |
| 912-124550¶ |  | 47.2 (1198) |  |
| 912-124551¶ |  | 57.2 (1452) |  |
| 912-124552¶ |  | 65.2 (1655) |  |
| 912-218283¶(1) | Empty Cabinet Length In. (mm) | 27.2 (690) |  |
| 912-218284¶(1) |  | 37.2 (944) |  |
| 912-218285¶(1) |  | 47.2 (1198) |  |
| 912-218286¶(1) |  | 57.2 (1452) |  |
| 912-218287¶(1) |  | 65.2 (1655) |  |
| 912-124553¶ | Recessed Trim Kit Heater Length In. (mm) (CAI Only Option F Required) | 27.2 (690) |  |
| 912-124554¶ |  | 37.2 (944) |  |
| 912-124555¶ |  | 47.2 (1198) |  |
| 912-124556¶ |  | 57.2 (1452) |  |
| 912-124557¶ |  | 65.2 (1655) |  |
| 912-124561¶(1) | Control Box Heater Length In. (mm) | 12 (305) |  |
| 912-124562 | 24V Relay Kit, Single-pole, 240V, 22 Amp; 277V, 19 Amp |  |  |
| 912-124563 | 24V Relay Kit, Double-pole, 240V, 25 Amp; 480V, 12.5 Amp |  |  |
| 912-124566 | 24V Relay Kit with Transformer, 208V, 22 Amp |  |  |
| 912-124567 | 24V Relay Kit with Transformer, 240V, 22 Amp |  |  |
| 912-124568 | 24V Relay Kit with Transformer, 277V, 19 Amp |  |  |
| 912-224767 | Tamperproof Single-pole Thermostat Kit |  |  |
| 912-224768 | Tamperproof Double-pole Thermostat Kit |  |  |

¶ Standard colors - Add W for white finish or A for almond finish to the end of part number.

Unit with Grille on Top

Rear View

Unit with Grille on Front (Option F)

Side View

Bottom View

Standard Construction Features

Heating Elements – Stainless steel elements with aluminum fins float on high temperature nylon bushings for quiet operation.

Housing – Cabinet is constructed of 20-gauge steel with a 16-gauge steel front cover.  The unit has a polyester powder paint finish in white or almond.  Mounting holes are provided along the back of the cabinet for wall installation.

Inlet/Outlet Grilles – The fresh air inlet grille is located on the front of the unit.  An extruded aluminum outlet grille discourages tampering with the heating elements.

Built-in Controls – Linear limit, automatic reset thermal cutout.

Rough In Dimensions – Heater Length + 1” wide x 21” high x 6” deep.

These units are not for residential use in the United States.