Built-in thermostat is not included.

| Watts | Volts | Total Amps (1) | CFM | Approximate Air Temperature Rise oF (oC) | Weight lb (kg) | Catalog Number |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 500 | 120 | 4.6 | 40 | 40 (22) | 9 (4) | HX-930U00500B¶ |  |
| 500/375 | 240/208 | 2.3/2.0 | 40 | 40/30 (22/17) | 9 (4) | HX-930U00500V¶ |  |
| 750 | 120 | 6.7 | 40 | 60 (33) | 9 (4) | HX-930U00750B¶ |  |
| 750/563 | 240/208 | 3.3/2.9 | 40 | 60/45 (33/25) | 9 (4) | HX-930U00750V¶ |  |
| 1000 | 120 | 8.7 | 40 | 80 (44) | 9 (4) | HX-930U01000B¶ |  |
| 1000/750 | 240/208 | 4.5/3.8 | 40 | 80/60 (44/33) | 9 (4) | HX-930U01000V¶ |  |
| 1250 | 120 | 10.8 | 80 | 50 (28) | 9 (4) | HX-930U01250B¶ |  |
| 1250/938 | 240/208 | 5.4/4.7 | 80 | 50/37 (28/21) | 9 (4) | HX-930U01250V¶ |  |
| 1500 | 120 | 12.9 | 80 | 60 (33) | 9 (4) | HX-930U01500B¶ |  |
| 1500/1125 | 240/208 | 6.5/5.6 | 80 | 60/45 (33/25) | 9 (4) | HX-930U01500V¶ |  |
| 2000 | 208 | 9.8 | 80 | 80 (44) | 9 (4) | HX-930U02000C¶ |  |
| 2000/1500 | 240/208 | 8.5/7.4 | 80 | 80/60 (44/33) | 9 (4) | HX-930U02000V¶ |  |

(1) Total Amps = Heating element amps and motor amps.

All models listed are single-phase.

¶ Standard colors - Add W for white finish or A for almond finish to the end of catalog number.

Factory Built-in Options

| Code | Description |  |
| --- | --- | --- |

| D3 | Disconnect Switch, 277V, Double-pole, 20 Amp |  |
| --- | --- | --- |
| T1 | Tamperproof Thermostat, Single-pole, 17 Amp |  |
| T2 | Tamperproof Thermostat, Double-pole, 17 Amp |  |
| T5 | Adjustable Thermostat, Single-pole, 17 Amp |  |
| T6 | Adjustable Thermostat, Double-pole, 17 Amp |  |

Double-pole thermostats include positive off feature.

Field-Installed Options (shipped loose for field Installation into heater)

| Catalog Number | Description |  |
| --- | --- | --- |
| 930-166766¶ | Surface Mounting Box |  |
| 930-166767¶ | Adjustable Thermostat Kit, Single-pole, 17 Amp |  |
| 930-166768¶ | Tamperproof Thermostat Kit, Single-pole, 17 Amp |  |
| 930-166769¶ | Adjustable Thermostat Kit, Double-pole, 17 Amp |  |
| 930-166770¶ | Tamperproof Thermostat Kit, Double-pole, 17 Amp |  |

¶ Standard colors - Add W for white finish or A for almond finish to the end of catalog number.

3"

3"

14 1/8"

16"

7 3/16"

8 1/8"

3"

13 7/8"

7 1/16"

8 1/8"

16"

Recessed Mounting

Optional Surface Mounting

Wall

Opening

Surface

Box

Heater

Grille

Architect’s and Engineer’s Specifications

The specified heating equipment shall include an electric, fan-forced air wall heater suitable for space heating as manufactured by HEATREX.  The wall heater shall be designed for wall recess or surface mounting.  Heaters shall be third party approved to UL standard 2021.  CSA-US or equivalent is acceptable.

Heater Housing shall be constructed from heavy 20 gauge steel.

Grille shall have a white or almond epoxy/powder paint finish.  Grille openings shall be less than 0.25” to discourage tampering with the elements (pencil-proof).  Contact factory for custom colors.

Heater Element shall be of finned tubular type.

Fan and Motor shall be thermally protected and have permanently lubricated ball bearings.  Fan shall operate at 40 CFM for heaters up to 1000W and 80 CFM for all other models.

Thermal Cutout shall be of the bi-metal type and built into the system.

Rough In Dimensions All heaters: 14-1/8” wide x 7-3/16” high x 3” deep.

900 Series Heaters

9XXXXXXXXX A - XXX

Add all desired factory built-in options:

See catalog and pricing sheets for list of options

Add the finish color desired:

See catalog and pricing tables for color availability

Standard Colors:

A = Almond, W = White (when available),

Select the catalog number for the heater from the listing