Adjustable thermostat is included.

A hole plug is provided for tamperproof installations.

| Watts | Volts | Total Amps (1) | CFM | Approximate Air Temperature Rise oF (oC) | Weight lbs (kg) | Catalog Number |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1500/1125 | 240/208 | 6.6/5.8 | 160 | 30/22 (17/12) | 24 (11) | HX-932U01500V¶ |  |
| 1500 | 120 | 12.9 | 160 | 30 (17) | 24 (11) | HX-932U01500B¶ |  |
| 1500 | 277 | 5.8 | 160 | 30 (17) | 28 (13) | HX-932U01500N¶ |  |
|  | 480 | 3.5 | 160 | 30 (17) | 28 (13) | HX-932U01500T¶ |  |
| 2000/1500 | 240/208 | 8.7/7.6 | 160 | 40/30 (22/17) | 24 (11) | HX-932U02000V¶ |  |
| 2000 | 208 | 10.0 | 160 | 40 (22) | 24 (11) | HX-932U02000C¶ |  |
|  | 277 | 7.6 | 160 | 40 (22) | 28 (13) | HX-932U02000N¶ |  |
|  | 480 | 4.6 | 160 | 40 (22) | 28 (13) | HX-932U02000T¶ |  |
| 3000/2250 | 240/208 | 12.9/11.2 | 160 | 60/45 (33/25) | 24 (11) | HX-932U03000V¶ |  |
| 3000 | 277 | 11.2 | 160 | 60 (33) | 28 (13) | HX-932U03000N¶ |  |
|  | 480 | 6.7 | 160 | 60 (33) | 28 (13) | HX-932U03000T¶ |  |
| 4000/3000 | 240/208 | 17.0/14.8 | 160 | 80/60 (44/33) | 24 (11) | HX-932U04000V¶ |  |
| 4000 | 208 | 19.6 | 160 | 80 (44) | 24 (11) | HX-932U04000C¶ |  |
|  | 277 | 14.8 | 160 | 80 (44) | 28 (13) | HX-932U04000N¶ |  |
|  | 480 | 8.7 | 160 | 80 (44) | 28 (13) | HX-932U04000T¶ |  |
| 4800/3600 | 240/208 | 20.4/17.7 | 160 | 96/72 (53/40) | 24 (11) | HX-932U04800V¶ |  |
| 4800 | 208 | 23.5 | 160 | 96 (53) | 28 (13) | HX-932U04800C¶ |  |
|  | 277 | 17.7 | 160 | 96 (53) | 28 (13) | HX-932U04800N¶ |  |
|  | 480 | 10.4 | 160 | 96 (53) | 28 (13) | HX-932U04800T¶ |  |
| 6000/4500 | 240/208 | 25.4/22.0 | 320 | 60/45 (33/25) | 50 (23) | HX-932U06000V¶ |  |
| 6000 | 277 | 22.1 | 320 | 60 (33) | 50 (23) | HX-932U06000N¶ |  |
|  | 480 | 12.9 | 320 | 60 (33) | 50 (23) | HX-932U06000T¶ |  |
| 8000/6000 | 240/208 | 33.7/29.2 | 320 | 80/60 (44/33) | 50 (23) | HX-932U08000V¶ |  |
| 8000 | 208 | 38.9 | 320 | 80 (44) | 50 (23) | HX-932U08000C¶ |  |
|  | 277 | 29.3 | 320 | 80 (44) | 50 (23) | HX-932U08000N¶ |  |
|  | 480 | 17.1 | 320 | 80 (44) | 50 (23) | HX-932U08000T¶ |  |
| 12000/9000 | 240/208/3 | 28.9/25.0 | 480 | 80 (44) | 90 (41) | HX-932U12000P¶ |  |
| 12000 | 208/3 | 33.7 | 480 | 80 (44) | 90 (41) | HX-932U12000D¶ |  |
|  | 240/3 | 29.3 | 480 | 80 (44) | 90 (41) | HX-932U12000K¶ |  |
|  | 277 | 43.7 | 480 | 80 (44) | 90 (41) | HX-932U12000N¶ |  |
|  | 480 | 25.4 | 480 | 80 (44) | 90 (41) | HX-932U12000T¶ |  |
|  | 480/3 | 14.8 | 480 | 80 (44) | 90 (41) | HX-932U12000U¶ |  |

(1) Total Amps = Heating element amps and motor amps.

All models listed are single-phase unless otherwise specified.  Other voltages available.  Consult factory.

¶ Standard colors - Add W for white finish or A for almond finish to the end of catalog number.

Factory Built-in Options

| Code | Description |  |
| --- | --- | --- |
| D1 | Disconnect Switch, 600V, Three-pole, 40 Amp |  |
| D2 | Disconnect Switch, 600V, Three-pole, 80 Amp |  |
| D3 | Disconnect Switch, 277V, Double-pole, 20 Amp |  |
| R1 | 24 Volt Relay (2) |  |
| R2 | 24 Volt Relay with Transformer (2) |  |
| S3 | Fan On/Auto Switch |  |

(2) A built-in thermostat will not be supplied when option “R1” or “R2” are selected. Contact factory if built-in thermostat is required with these options.

Field-Installed Options

(shipped loose for field Installation into heater)

| Catalog Number | Description |  |
| --- | --- | --- |
| 932-124500¶ | Surface Mounting Box (1500-4800 W) |  |
| 932-158211¶ | Surface Mounting Box (6000-8000 W) |  |
| 932-158212¶ | Surface Mounting Box (12000 W) |  |
| 932-146878¶ | 1” Semi Recessed Trim Kit (1500-4800 W) |  |
| 932-166532¶ | 1” Semi Recessed Trim Kit (6000-8000 W) |  |
| 932-166534¶ | 1” Semi Recessed Trim Kit (12000 W) |  |
| 932-153670¶ | 2” Semi Recessed Trim Kit (1500-4800 W) |  |
| 932-166533¶ | 2” Semi Recessed Trim Kit (6000-8000 W) |  |
| 932-166535¶ | 2” Semi Recessed Trim Kit (12000 W) |  |

¶ Standard colors - Add W for white finish or A for almond finish to the end of catalog number.

Grille Dimensions

1,500-4800 Watts

Side

View

Front View

(without grille)

Front View

Side

View

6,000-8,000 Watts

12,000 Watts

Heater Dimensions

Required Wall Depth Opening

Side View

Architect’s and Engineer’s Specifications

The specified heating equipment shall include an electric, fan-forced air wall heater suitable for space heating as manufactured by HEATREX.  The wall heater shall be designed for wall recess or surface mounting.  Heaters shall be third party approved to UL standard 2021.  CSA-US or equivalent is acceptable.

Heater Housing shall be constructed from heavy 18 gauge steel.

Grille shall have a white or almond epoxy/powder paint finish.  Grille openings shall be less than 0.25” to discourage tampering with the elements (pencil-proof).  Contact factory for custom colors.

Heater Element shall be of finned tubular type.

Fan and Motor shall be totally enclosed and have permanently lubricated ball bearings.  Fan shall operate at 160 CFM minimum.

Fan Over-ride shall purge heater of residual heat to prevent an over heat condition.

Thermal Cutout shall be of the bulb and capillary type and built into the system.

Thermostat is included as standard.  Adjustable from 32-120⁰F, comes complete with an adjustable knob and a hole plug for tamperproof installations..

Disconnect Switch is offered as an option and is built into the back of the system.  The disconnect switch shall provide positive disconnect of the main power source.

Low Voltage Relays with or without transformers are available built-in or supplied separately as kits.

Rough In Dimensions

- 1500/1125 – 4800 Watt heaters: 14-1/2” wide x 19-7/8” high x 4-1/2” deep.

- 6000/4500 – 8000 Watt heaters: 30-3/16” wide x 19-7/8” high x 4-1/2” deep.

- 12000/9000 – 12000 Watt heaters: 46-5/8” wide x 19-7/8” high x 4-1/2” deep.