Recessed Mounting

| Watts | Volts | Total Amps(1) | CFM | Approximate Air Temperature Rise oF (oC) | Weight lb (kg) | Catalog Number |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 2000 | 208/1 | 10.3 | 450 | 14 (8) | 31 (14) | HX-937U02000C¶ |  |
|  | 208/3 | 6.3 | 450 | 14 (8) | 31 (14) | HX-937U02000D¶ |  |
|  | 240/1 | 9.0 | 450 | 14 (8) | 31 (14) | HX-937U02000J¶ |  |
|  | 240/3 | 5.5 | 450 | 14 (8) | 31 (14) | HX-937U02000K¶ |  |
|  | 277/1 | 7.9 | 450 | 14 (8) | 31 (14) | HX-937U02000N¶ |  |
|  | 480/1 | 4.9 | 450 | 14 (8) | 31 (14) | HX-937U02000T¶ |  |
|  | 480/3 | 3.1 | 450 | 14 (8) | 31 (14) | HX-937U02000U¶ |  |
| 3000 | 208/1 | 15.1 | 450 | 21 (12) | 31 (14) | HX-937U03000C¶ |  |
|  | 208/3 | 9.0 | 450 | 21 (12) | 31 (14) | HX-937U03000D¶ |  |
|  | 240/1 | 13.2 | 450 | 21 (12) | 31 (14) | HX-937U03000J¶ |  |
|  | 240/3 | 7.9 | 450 | 21 (12) | 31 (14) | HX-937U03000K¶ |  |
|  | 277/1 | 11.5 | 450 | 21 (12) | 31 (14) | HX-937U03000N¶ |  |
|  | 480/1 | 7.0 | 450 | 21 (12) | 31 (14) | HX-937U03000T¶ |  |
|  | 480/3 | 4.3 | 450 | 21 (12) | 31 (14) | HX-937U03000U¶ |  |
| 4000 | 208/1 | 19.9 | 450 | 28 (16) | 31 (14) | HX-937U04000C¶ |  |
|  | 208/3 | 11.8 | 450 | 28 (16) | 31 (14) | HX-937U04000D¶ |  |
|  | 240/1 | 17.4 | 450 | 28 (16) | 31 (14) | HX-937U04000J¶ |  |
|  | 240/3 | 10.3 | 450 | 28 (16) | 31 (14) | HX-937U04000K¶ |  |
|  | 277/1 | 15.1 | 450 | 28 (16) | 31 (14) | HX-937U04000N¶ |  |
|  | 480/1 | 9.0 | 450 | 28 (16) | 31 (14) | HX-937U04000T¶ |  |
|  | 480/3 | 5.5 | 450 | 28 (16) | 31 (14) | HX-937U04000U¶ |  |
| 5000 | 208/1 | 24.7 | 450 | 35 (19) | 31 (14) | HX-937U05000C¶ |  |
|  | 208/3 | 14.6 | 450 | 35 (19) | 31 (14) | HX-937U05000D¶ |  |
|  | 240/1 | 21.5 | 450 | 35 (19) | 31 (14) | HX-937U05000J¶ |  |
|  | 240/3 | 12.7 | 450 | 35 (19) | 31 (14) | HX-937U05000K¶ |  |
|  | 277/1 | 18.8 | 450 | 35 (19) | 31 (14) | HX-937U05000N¶ |  |
|  | 480/1 | 11.1 | 450 | 35 (19) | 31 (14) | HX-937U05000T¶ |  |
|  | 480/3 | 6.7 | 450 | 35 (19) | 31 (14) | HX-937U05000U¶ |  |

(1) Total Amps = Heating element amps and motor amps.

¶ Add W to end of catalog number for white finish or add A for almond finish.

| Factory Built-in Options Code | Description |  |
| --- | --- | --- |
| D1 | Disconnect Switch 600V, Three-pole, 40 Amp |  |
| D2 | Disconnect Switch 600V, Three-pole, 80 Amp |  |
| D3 | Disconnect Switch 277V, Doube-pole, 20 Amp |  |
| R1 | 24V Control Relay |  |
| R2 | 24V Control Relay with Transformer |  |
| S3 | Summer Fan Switch and Pilot Light |  |
| S5 | Summer Fan 24V Relay for Remote Switching and Pilot Light (Switch not included) |  |
| S6 | Summer Fan 24V Relay for Remote Switching and Pilot Light (Switch not included) |  |
| T1 | Tamperproof Thermostat |  |
| X | 120V Control, fused secondary and grounded |  |

Field-Installed Options

(shipped loose for field Installation into heater)

| Catalog Number | Description |  |
| --- | --- | --- |
| 936-158478¶ | Tamperproof thermostat kit |  |
| 936-218269 | 24 Volt Control Relay Kit |  |
| 936-218270 | 24 Volt Relay Kit with Transformer Kit |  |

¶ Add W to end of catalog number for white finish or add A for almond finish.

937 Series Surface Mounting

2,000-5,000 Watt Heaters

937 Series Recessed Mounting

How to Order

937 Series Surface Mounting

2,000-5,000 Watt Heaters

9XXXXXXXXX   A - XXX

Add all desired factory built-in options:

See catalog and pricing sheets for list of options

Add the finish color desired:

See catalog and pricing tables for color availability

Standard Colors:

A = Almond, W = White (when available),

Select the catalog number for the heater from the listing

Architect’s and Engineer’s Specification

Heating Elements – Stainless steel tubular elements with aluminum fins.

Outlet Grille – The grille is made of 20-gauge galvanized steel and is finished with a polyester powder paint in white or almond.

Built-in Controls – Automatic reset thermal cutout and fan delay relay.

Fan Motor – Quiet, direct drive aluminum fan and totally enclosed motor with lifetime lubricated ball bearings.

Installation Requirements – For best performance, ceiling heaters should be installed between 8 and 12-feet above the floor.

Rough In Dimensions –23” wide x 23” high x 6” deep.